## Slide 2: TD-3: GUIDE FOR REGULATORY INSPECTION OF AGEING MANAGEMENT AND LONG TERM OPERATION OF NPP
PREEV PROJECT: REGULATORY PRACTICES ON AGEING AND LIFE EXTENSION
IAEA CONSULTANTS MEETING
VIENNA, 11-13 APRIL 2012
J.M. FIGUERAS (CSN, SPAIN)

## Slide 3: PREEV PROJECT TD-3: GUIDE FOR REGULATORY INSPECTION OF AGEING MANAGEMENT AND LONG TERM OPERATION OF NPP
Objective.-
To establish guidelines for regulatory inspection of ageing management (AM) analyses and reviews and long term operation (LTO) conditions of structures, systems and components (SSCs) of NPPs
based on criteria given in TD-1 “Guide for regulatory criteria on AM and LTO of NPP”
To verify regulatory assessment results obtained through application of guidelines in TD-2 “Guide for assessment of AM and LTO of NPP”
Scope.-
Applicable to NPPs types PWR, BWR, CANDU y PHWR, in all operating conditions

## Slide 4: PREEV PROJECT TD-3: GUIDE FOR REGULATORY INSPECTION OF AGEING MANAGEMENT AND LONG TERM OPERATION OF NPP
Inspection types.-
Guideline TD-3 defines 4 regulatory inspection types, depending on the ageing management period:
During design life, PLiM (usually 30-40 years):
Type 1: verifications on definition and development of a PLiM or ageing management analysis and review (AMR), related with methodology, organization, scoping and screening of SSC, materials, environments, degradatory mechanisms and effects, definition of ageing management programmes (AMP), obsolescence, etc.
In principle it is expected only one inspection, at beginning of plant life.
Type 2: routine and periodic verifications on control, application and maintenance of defined AMPs in the AMR, performing document verifications as well as in plant SSCs walkdowns
Yearly or biennial frequency, for document verifications and quarterly or half yearly for in plant walkdowns

## Slide 5: PREEV PROJECT TD-3: GUIDE FOR REGULATORY INSPECTION OF AGEING MANAGEMENT AND LONG TERM OPERATION OF NPP
During long term operation, LTO (usually after 30-40 years):
Type 3: verification on definition, scope and development of Integrated Plant Assessment (IPA) [PIEGE in spanish] or its equivalent Plant Life Extension [PLEX] Analysis for CANDU, normally in same aspects as in AMR
In principle it is expected also only one inspection, divided in several blocks as needed, at end of design life and before beginning of plant life extension (2-3 years before LTO)
Type 4: routine and periodic verifications on control, application and maintenance of defined AMPs in the IPA and the long term review plan [LT-AMR], or its equivalents PLEX and Safety improvement plan [SIP] for CANDU performing document verifications as well as in plant SSCs walkdowns
Yearly or biennial frequency, for document verifications and quarterly or half yearly for in plant walkdowns

## Slide 6: PREEV PROJECT TD-3: GUIDE FOR REGULATORY INSPECTION OF AGEING MANAGEMENT AND LONG TERM OPERATION OF NPP
Areas or aspects to be inspected.-
  Type 1 inspections (PLiM):
    Objective of the inspection
    Organizational and management aspects
    Structure of the licensee's organization in relation to ageing management
    Acquisition and recording of information related to ageing management
    Monitoring of the licensee’s accepted commitments and commitments introduced by RB (conditions, non-conformities, regulatory requirements, etc.)
    Scoping and screening of SSCs
    Results of application of the SSCs scoping and screening methodology
    Methodological aspects related to PLiM Plan analysis

## Slide 7: PREEV PROJECT TD-3: GUIDE FOR REGULATORY INSPECTION OF AGEING MANAGEMENT AND LONG TERM OPERATION OF NPP
    (Cont´d)
    Results of PLiM Plan analysis
    Process for identification and resolution of Generic Safety Issues (GSI) associated with ageing management
    Monitoring of improvement proposals (IP)
    Design modifications (DMs) and replacement of equipment associated with ageing management
    Supporting documents review
    Obsolescence management
  Type 3 inspections (LTO):
    Same issues as in Type 1, but related to IPA organization, preparation, development and results
    Inclusion of time limited ageing analysis (TLAA)
    Reference to phases and content of a PLEX project for LTO, in case of CANDU

## Slide 8: PREEV PROJECT TD-3: GUIDE FOR REGULATORY INSPECTION OF AGEING MANAGEMENT AND LONG TERM OPERATION OF NPP
Types 2 and 4 inspections (PLiM and LTO):
Objective of the inspection
Organizational and management aspects
Scoping and screening of SSCs
Methodological aspects related to PLiM (or LT-AMR in case of LTO) analysis
Results of PLiM or LT-AMR analysis
Process for Identification and Resolution of GSI associated with LTO ageing management
Monitoring of IPA or PLEX Improvement Proposals (IP)
Design modifications (DM) and replacement of equipment associated with LTO ageing management
Supporting documents review
Obsolescence management
TLAA (in case of LTO)
Periodic reports of PLiM or LT-AMR
Conditions of SSCs

## Slide 9: PREEV PROJECT TD-3: GUIDE FOR REGULATORY INSPECTION OF AGEING MANAGEMENT AND LONG TERM OPERATION OF NPP
List of Definitions and Acronyms, in coherence with other TDs 1,2 and 4
Figures 1 to 5 and Tables B and C explain particular aspects for ageing management and LTO in CANDU type or PWR/BWR/PHWR type reactors
Table A shows topics subject to regulatory inspection for each type of inspection (1, 2, 3 and 4)
As Annexes A, B, C, Guideline TD-3 includes Check Lists examples, for documents verification as well as for in plant walkdowns for SSCs

## Slide 10: PREEV PROJECT TD-3: GUIDE FOR REGULATORY INSPECTION OF AGEING MANAGEMENT AND LONG TERM OPERATION OF NPP
Main bibliography.-
IAEA safety standards:
Guide NS-G-2.12, 2009 (Ageing management)
Guide NS-G-2.10, 2003 (RPS)
Guide SS-17, 2008 (SALTO)
Report “Safety glossary and terminology for NS and RP”, 2007
Other technological countries rulemaking:
Rule 10CFR54, 1995 (USNRC) + NUREG-1800, NUREG-1801 and NEI-95-10
Rule 10CFR50.65, 2000 (USNRC)
Regulatory document RD-360-CANDU, 2008 (CSNC)

## Slide 11: PREEV PROJECT TD-3: GUIDE FOR REGULATORY INSPECTION OF AGEING MANAGEMENT AND LONG TERM OPERATION OF NPP
PREEV countries rulemaking:
Spanish CSN Safety Instruction IS-22 (2009), Safety Guide GS-1.10 (2008) + 2 internal procedures: PT-IV-105 (assessment) and 223 (inspection)
  Includes WENRA recommendations on ageing management
  Brazilian CNEN Standards NN 1.14 (2002), NN 1.26 (1997)